| Prepared for: John & Jane Lucky Buyer(s) Inspection Address: 130 OldhouseAve. Los Gatos, CA Cross Street: Squeakyclean Inspection Date: 3/18/98 | Represented by: Donna Salezagent Yor Realty Company 1234 Sucess Road Los Gatos, CA 95030 Telephone: (408) 358-1926, FAX: (408) 358-1977 |
| --- | --- |

At your request, a home inspection of the property at 130 Oldhouse Ave. was performed on 3/18/98.  WellHouse is pleased to submit the enclosed report.  Thanks again for selecting our company, we appreciate the opportunity to be of service.

Cosmetic considerations are not within the scope of this report.  Even the most comprehensive inspection cannot be expected to reveal every condition you may consider significant to your ownership.  You should examine the portions of this house that are of concern to you prior to closing, including appliances, interior wall coverings, floor coverings, levelness of floors, etc.  Furthermore, owning any building involves some risk and while we can give an excellent overview of the property, we can inspect only what is visually accessible.  Moving furniture or personal storage, lifting carpet,any dismantling, or lighting gas pilots are not within the scope of this inspection.  This report is not intended to be an exhaustive technical evaluation and should not be construed as identifying every possible condition. Conditions of a property over time can change or be changed.  The information contained within the report reflects the observations and opinions of the inspector at the time the inspection was performed with the general age and construction type taken into consideration.

Comments regarding possible observed conditions or recommendations are not intended as criticisms toward the building, rather, they are offered as a professional opinion pertaining to the present condition of the property.  Items may have been included in report which are referred to as upgrades.  These have been included where the inspector felt they might be beneficial to enhance the property.

This report was prepared for John & Jane Lucky.  In the event that the inspection report has been prepared for a seller, WellHouse is authorizing it’s use in assisting the seller to fill-out the property disclosures.  Furthermore, we will return to the property, for a fee, and perform a “walk-through” with a buyer to explain and clarify the content of the report. Your attention is directed to the Agreement For Home Inspection Services, a copy of which is attached.  It more specifically delineates the scope of the inspection and the limit of WellHouse’s liability in performing this inspection.

Sincerely,

Craig Moorhead

WellHouse Corporation, Building Inspections

# Table OF Contents

TABLE OF CONTENTS

1. OVERVIEW

2. UTILITY / SERVICE SHUT-OFF LOCATIONS

3. SITE & TOPOGRAPHY

4. STRUCTURE

5. ROOFING

6. EXTERIOR

7. DOORS & WINDOWS

8. GARAGE / PARKING

9. INTERIOR

10. PLUMBING

11. ELECTRICAL

12. MECHANICAL

13. CHIMNEY(S) & FIREPLACE(S)

14. INSULATION & VENTILATION

15. END

Notes

# 1 Overview

The property was a multi-level single family building which appeared to be approximately 103 years old when inspected.  It was this inspectors opinion that the general condition of the building when inspected was good with items noted within this report which were unsafe and needing attention.  The weather at the time of the inspection included dry conditions and a temperature of approximately 50 to 60 degrees.  Recent weather conditions prior to the date of inspection has been generally wet.  Evidence to indicate previous repair / modifications was visible at the time of inspection.  These changes may have required building permits from the local building department when installed, therefore, it is recommended that interested parties review pertinent building permits.  Generally, elements of construction need to comply with the locally adopted codes which were applicable at the time of installation and do typically vary between municipalities.  You should be aware that this building may have been built using products which may contain asbestos.  As stated by the Contractors State License Board in their contractors asbestos pamphlet: "Asbestos is a naturally occurring mineral fiber that has been used extensively in construction and many other industries.  Nearly every building contains asbestos in some form."  Positive identification of asbestos is beyond the scope of our inspection.  If specific identification or information is desired regarding asbestos, it is recommended that interested parties contact an expert in the field.

All pre-1978 buildings have a  possibility of containing lead.  Identification or determination of the presence of lead is beyond the scope of our inspection.  Testing for lead-paint is not mandatory, however, according to EPA regulations that went into effect in 1996, buyers of property do have the right to obtain professional testing for possible lead-paint.  Please read each section of this report, and feel welcome to call our office if you have questions.  Other report(s), that we were aware of at the time this report was prepared, included the pest control report and roofing report and engineering report.  It is recommended that you refer to these for additional information.  The inspection has been performed in a manner generally consistent with the standards of practice of the "American Society of Home Inspectors" (ASHI).  Effort has been put into the design and layout of this report so that it is clear and understandable.  It is organized into sections according to building systems.  Each section generally includes "description" paragraphs  (following the section heading) containing the items which were inspected and which contains information regarding the specific system (i.e.: plumbing).  When appropriate, cross references to other sections may have been included.  The "Observed Conditions" paragraph contains items which were inspected and warranted comment.  This may include comments for informational purposes, elements which need attention or repair, possible hazardous conditions, or items which were extraordinarily good.  A specific recommendation is included as part of an Observed Condition when the inspector felt it was warranted.  "General Comments" paragraphs are included when pertinent.

As a general note, the report may include references regarding further inspection and/or repair.  It is assumed that this would be performed by a qualified / licensed contractor, engineer and/or architect.  A contractor in this context is a licensed individual or company who performs construction and/or corrective work.  An engineer or architect if called upon, would provide in-depth further investigation prior to corrective work when / if needed and would provide in-depth study of a condition and dictate specific needed repairs which could then be performed by a contractor.

# 2 Utility / Service Shut-Off Locations

Electric:

The electrical utility service meter was located at the exterior left-front area with the main panel / disconnect located near the meter.  Refer to the electrical section of this report for additional information.

Gas:

Provisions for natural gas were noted.  A gas meter was located at the  exterior right-front area of the building.  The gas supply can be shut-off by turning the valve (located at the service line between the ground and the meter) 90 degrees.  It is a good idea, and strongly suggested, that a wrench be kept near the meter for quick access in the event of an emergency.

Water:

The water service shut-off valve was located at the back lower interior room of the building.  This appeared to be shut-off by turning the valve (located near the stove).  Service valves are seldom operated and may begin to leak if / when operated, therefore, these are not tested during the course of inspection.  The service piping leading to the house was not determined.

# 3 Site & Topography

Property:

Provisions for underground perimeter site drainage were noted at exterior and visible at a few places at the rain gutter down spouts and/or adjacent site locations.  No opinion was rendered regarding the effectiveness of the system and the drain emitter location(s) were not ascertained.

Flatwork:

The driveway was generally constructed of gravel.  Concrete flatwork was noted and included the walkways.  Tile flatwork was noted at the back patio.

Amenities:

A hot tub was installed at the property.  This was beyond the scope of the inspection and was not inspected, however, it is recommended to have a qualified technician inspect the unit.  Protection of the water area should be provided / maintained in order to control access for safety purposes, especially by small children.

Front Porch

An attached wood deck was noted at the exterior and had pier posts on piers.

Observed Site Conditions:

4  Cracks were noted in the walkway(s) surface which were up to 1/2 inch(es) wide.  While this is a common condition, repair and possible periodic maintenance of the cracks/gaps in the surface is recommended as a preventative maintenance item to eliminate possible tripping hazards.

5  The general condition of the tile patio(s) appeared to be very good.

General Site Comments:

6  As a preventative measure, water from the rain gutter downspouts should be diverted away from the building foundation.  Also, where applicable, the soil adjacent to the house should be sloped so water drains away from the building and possible gaps between the house and concrete flatwork should be periodically sealed to prevent moisture penetration.  These measures can help to stabilize the moisture in the soil and may help reduce possible future building settlement.

7  A masonry barbecue was installed at the property.  This was beyond the scope of the inspection and was not inspected.

8  A detached shed building/structure was noted at the property.  This was beyond the scope of the inspection and was not inspected.

9  Trees and/or foliage were noted near the building and/or roof surface.  The foliage should be kept trimmed to prevent contact with the building and will likely require periodic maintenance.

# 10 Structure

Foundation & Floors:

Unreinforced brick foundations were noted generally and appeared to be the original installation.  1X boards were installed over floor joist.

Roof/Ceilings & Walls:

The attic access scuttle was located at the upper interior and lower interior.  The general attic was examined during the course of inspection, however, it was viewed from the attic scuttle location only because of small physical clearance and insulation.  Conventional 2X wood framing was generally visible at the roof / ceiling structure.  The walls appeared to be conventional wood 2X4 framing installed generally.

Observed Structure Conditions:

11  The general condition of the building structure appeared to be good for its age.  However, items were noted which were in need of attention, refer to the sections below for related comments.  Refer to the structural report for information and comments.

12   Unreinforced brick foundations were noted generally and appeared to be the original installation.  A significant degree of deterioration was noted to the brick mortar in the foundation.  This was most notable at the left front exterior of the building.  Refer to the engineering reports for related comments.

13   Unevenness was noted at various floor locations throughout the house.  This appeared to be due to additions, characteristics pertaining to the age of the building and modified/converted porch locations which were originally built sloped.

14   Evidence of recently constructed foundations were noted at the left exterior near  the back family room/garage.

Observed Structure Conditions: (continued)

15   Non-standard construction was noted at the back porch roof framing.

16  Garage: no visible provisions for diagonal bracing was noted at the wall above/adjacent to the main garage door. Refer to the earthquake handbook for additional information.  Minimal provisions for diagonal bracing to the structure below the family room/bathroom located over the garage was noted.  Upgrading/strengthening the building in this area is strongly recommended.

17   Significant notching was noted to the floor framing of the family room/bathroom to accommodate a let-in diagonal brace.  This was visible at the ceiling of the garage.  While no evidence of cracked joists related to the notching was visible when inspected, the installations have significantly reduced the strength of the floor joists where notched.

18   Entry porch: white deposits/possible fungus growth was noted to the wood framing below the entry porch.  This appeared to be due to moist conditions and was most notable at the perimeter location.  The area affected by this condition was relatively small compared to the size of the porch.  Refer to the pest control report for possible comments and/or opinions.

General Structure Comments:

19  The left crawl space area forward of the basement was not accessible because of a minimal sized access opening.

20  Refer to the engineering reports for comments and recommendations.

# 21 Roofing

Roofing Material:

General Roof

Wood shakes were installed at the roof surface and appeared to be unknown layer(s) of roofing when inspected.  Shakes are normally interlaced with roof felt (an asphalt impregnated paper), and on roof slopes of 4 in 12 and greater.  The purpose of the roof felt is to provide a water barrier beneath the shakes.  The felt is the actual moisture barrier and, therefore, it is important that the felt paper remain intact and protected from direct sunlight since the ultra-violet light will cause accelerated deterioration of the felt.  Common maintenance for a shake roof consists of periodically shimming between various shakes to cover areas of exposed / visible roof felt and will usually occur where a hole or crack in a shake aligns with a keyway of the lower course of shakes.  Maintenance is typically recommended every few years once the roof is 6 to 8 years old  with the projected serviceable life of the roof being 20 to 25 years.

Flashing:

Locations requiring roof flashing as a means of water proofing was noted at the juncture of the roof with plumbing / mechanical vent(s) and upper house wall(s).

Other Roofing:

An exterior deck surface was exposed to the weather and installed at the upper back area.  Evidence of leakage was noted and was visible in the storage closet below the deck.  Repair is needed.  Refer to the pest control report for possible comments.

Observed Roofing Conditions:

22  Plumbing vent(s) / flashing were noted which had non-rated pipe wrap tape and deteriorated sealant and was visible in numerous place(s).  Repair is needed for these to be water tight.

23  Missing flashing was noted at the juncture of the roof and upper wall(s) when inspected and may allow moisture penetration.

24  General Roof: The wood shake roof covering appeared to have wear characteristics to indicate the age being approximately 10 to 12 year(s).

25  Front Roof: The roofing felt was generally improperly installed and was placed about 8 inches too low.

General Roofing Comments:

26  General Roof: Further inspection of the roof by a licensed roofing contractor is recommended.

# 27 Exterior

Walls / Eaves:

Wood siding was installed at the general exterior wall surfaces.  Since wood siding is a natural material, there will likely be variations which may include slight warping and/or curling / cupping in the material.  Painted plywood siding was installed at the remodeled exterior wall surfaces.  This is a manufactured wood product which is commonly used in modern construction.  Because it is a manufactured product, it is generally more uniform than traditional wood siding boards.  However, it is generally more susceptible to weathering and possible delamination if left unprotected and should be kept well painted to prevent premature deterioration and/or damage.  Painted wood shingle siding was installed at the general exterior wall surfaces.  Since wood shingles are a natural material, there will likely be variations which may include slight curling in the material.

Posts / Columns:

Wood support post(s) and column(s) were installed at the exterior and visible at the front.

Rain Gutters / Downspouts:

Provisions for roof drainage included metal rain gutters installed at various roof eave locations with the purpose of collecting water which drains from the roof surface.  Metal down spouts were installed at the exterior.  These function to lead water from the roof drains to the ground and/or site drainage if applicable.

Observed Exterior Conditions:

28  The trunk from a nearby tree was in contact with the building at the right-front exterior.  Modification to the building is recommended to prevent contact with the building and cleaning the roof surface of foliage / debris should be done as periodic maintenance to prevent possible related problems and/or premature deterioration of the roofing material.

29  The roof drain downspout(s) at the back-left exterior were corroded and appeared to be due to current and/or previous leakage.

30  Moisture stains were noted at the exterior closet below the upper back porch and/or stair which appeared to be due to leakage through the decking.  Further inspection is recommended.

31  Unsealed joints/gaps were noted at the wood siding including the various and left-front exterior wall(s).  Sealing these locations as periodic maintenance is recommended to prevent moisture intrusion and premature deterioration .

32  Moisture penetration/damage was noted at the wood siding including the front exterior.  Removal of the damaged wood and repair is needed.  Refer to the pest control report for possible comments and/or opinions.

33  Direct contact of the wood siding and soil was noted at the front and left to exterior.  Correction of this condition is recommended to prevent premature deterioration/damage to the siding.  Refer to the pest control report for possible comments and/or opinions.

Observed Exterior Conditions: (continued)

34  Moisture penetration/delamination was noted at the plywood siding including the back-right exterior.  Removal of the damaged wood and repair is needed.  Refer to the pest control report for possible comments and/or opinions.

35  Corrosion was noted at the joints in the rain gutters visible at various locations and is an indication of previous and/or current leaking.

36  The upper back porch railings / balusters were spaced with opening larger than 4 or 6 inches and care should be taken if / when small children are present.

# 37 Doors & Windows

Doors:

A single, glass and wood door was installed at the entry.  A hollow core wood door was installed at the exterior storage closet.  Hinged wood door(s) were installed at the garage to provide automobile access.

Hinged closet doors were installed.  The interior passage doors were generally wood.

Windows:

Single pane glass was installed generally at the  windows.  Wood framed double hung windows were installed at the general exterior wall locations.  This type of window is designed for both the upper and lower sashes to open, however, it is not uncommon for the upper sashes to be painted or stuck closed due to infrequent operation.

Observed Doors/Windows Conditions:

38  The exterior closet door had deterioration and was delaminated at the time of inspection and was in need of repair and/or replacement.  Refer to the pest control report, where applicable, for possible comments.

39  The dead bolt of the entry door was locked and the door not tested when inspected/tested.

40  Living Room: The passage door strikes the jamb and doesn't close when operated / tested.

41  Upstairs Hall Bath: The window located at the wall of the shower had no visible emblems to indicate safety glass. Building standards require safety glass at windows when located within 5 feet of the standing surface of the shower.

42  Varied: The top window sash counterbalance mechanism assembly was not operating properly and allowed the window to open/operate uncontrolled.  Care should be taken when using the window to prevent pinched finger tips and/or breaking the glass.  Repair this condition is recommended.

Observed Doors/Windows Conditions:(continued)

43  Varied: The window sash did not open when tested and was in need of repair /maintenance.

44  Varied: A missing latch was noted at the window sash and was in need of minor repair.

45  Varied: Non-operable window sash(es) were noted which appeared to be due being painted shut.

46  Varied: Cracked glass was noted at the window(s).  Refer to a qualified tradesperson for repair.

47  Master Bath: The window located at the wall of the tub-shower had no visible emblems to indicate safety glass. Building standards require safety glass at windows when located within 5 feet of the standing surface of the tub-shower.

48  Upstairs Hall Bath: The window located at the wall of the shower had no visible emblems to indicate safety glass. Building standards require safety glass at windows when located within 5 feet of the standing surface of the shower.

# 49 Garage / Parking

Fire Resistive Construction:

There was no visible provision for fire resistive construction at the common wall(s) and ceiling area(s) between the garage and house / interior.  However, this building may have been constructed prior to current standards requiring firewall separation between the garage and living areas.  The purpose of a firewall is to provide a construction type which has been tested to be fire resistive and therefore installation is recommended as a future upgrade.

Other Garage / Parking:

Concrete was installed at the floor of the garage.  Severely limited access for inspection of the general areas of the attached garage interior was noted because of personal storage and automobile(s);  no opinion was rendered for the areas which were not visible when inspected.

Observed Garage / Parking Conditions:

50  An incomplete firewall was noted because of missing drywall at the basement wall area of the garage.

51  Refer to the electrical and structural section for comments.

# 52 Interior

General:

Carpeting was installed at the varied finish flooring.  Wood was installed at the varied finish flooring.  Ceramic tile was installed at the varied finish flooring.  The walls and ceiling surfaces appeared to be generally wood and drywall and plaster.

Kitchen

Ceramic tile counters and wood cabinets were generally installed at the kitchen.  A cast-iron enameled sink was installed in the kitchen counter.  A built-in gas with electric ignition stove top was installed.  An exhaust hood was installed at the stove top area.  A built-in electric oven was installed.  A garbage disposal unit was noted at the sink with an electrical manual disconnect (usually a utility cord) installed.  A dishwasher was located in the kitchen and had a manual electrical disconnect installed and had an airgap not installed, see below.

2nd Kitchen

A cast-iron enameled sink was installed in the kitchen counter.  A combination gas with standing pilot - stove/oven appliance was installed.  A dishwasher was located in the kitchen and had a manual electrical disconnect installed and had an airgap not installed, see below.

Bathroom(s):

Master Bath

A triplex (three prong) electrical receptacle(s) was installed.  Refer to the electrical section of this report for comments.  An openable window was installed to provide ventilation into the bathroom.  A bath tub/shower unit was installed.  Ceramic tile was installed at the tub/shower walls.  A shower curtain was installed at the to provide a moisture barrier to prevent water from splashing to adjacent areas when used.  The installation of a shower enclosure in place of a curtain is recommended as a preventative upgrade.

Upstairs Hall Bath

A triplex (three prong) electrical receptacle(s) was installed.  Refer to the electrical section of this report for comments.  An openable window was installed to provide ventilation into the bathroom.  A cultured marble counter and wood vanity was installed.  A stall shower was installed.  Ceramic tile was installed at the shower walls.  Shower enclosure door(s) were installed at the shower.  Emblems which appeared to indicate safety glazing were noted at the corner of the glass.  The enclosure should be periodically caulked / maintained to prevent water from leaking through the joints and causing damage to adjacent materials.

Downstairs Bath

A triplex (three prong) electrical receptacle(s) was installed.  Refer to the electrical section of this report for comments.  An openable window was installed to provide ventilation into the bathroom.  A wood counter and wood vanity was installed at the bathroom.  A bath tub/shower unit was installed.  Fiberglass was installed at the tub/shower walls.  A shower curtain was installed at the to provide a moisture barrier to prevent water from splashing to adjacent areas when used.  The installation of a shower enclosure in place of a curtain is recommended as a preventative upgrade.

Bathroom (at the studio)

An openable window was installed to provide ventilation into the bathroom.  A ceramic tile counter and wood vanity was installed at the bathroom.  A GFCI (Ground Fault Circuit Interrupt) protected electrical receptacle(s) was noted with the device located at the outlet.  GFCI's are safety devices and should be tested for proper operation at least once per month.  The GFCI operated and tripped when tested.  A stall shower was installed.  Ceramic tile was installed at the shower walls.  A shower curtain was installed at the to provide a moisture barrier to prevent water from splashing to adjacent areas when used.  The installation of a shower enclosure in place of a curtain is recommended as a preventative upgrade.

Observed Interior Conditions:

53  Master Bath: The juncture of the vinyl flooring and the bath tub was unsealed and/or had deteriorated/missing caulking which may allow moisture to penetrate to the underlayment below.  Resealing is recommended as a preventative measure and should be included as periodic maintenance.

54  Kitchen: An airgap was not installed as part of the dishwasher drain assembly when inspected.  It is generally required and is intended to prevent possible contamination of the water supply by preventing drain water from siphoning back into the unit.  Installation of an airgap is recommended.

55  2nd Kitchen: The stove / oven was not tested at the time of inspection because of the pilots were turned off.  Testing the unit prior to close of escrow is recommended.

56  Downstairs Bath: The tub shower faucet assembly was loose and may not be secured to the wall framing when inspected.  This was a mechanical condition which did not prevent operating the unit when inspected.

General Interior Comments:

57  While smoke detector(s) were noted at the interior when inspected, it was not tested for operation when tested.  Periodic testing of smoke detectors is recommended.  It is recommended to have operable smoke detectors located at the interior of each bedroom and at the hallway adjacent to the bedroom areas.  While the addition of smoke detectors to the bedrooms may be an upgrade, these are now required to be added when improvements to the house exceed $1,000.  It is also wise and recommended to have a fire extinguisher accessible at the interior of the house as a safety upgrade measure.

58   It is recommended to have a qualified contractor repair/modify as needed.  Refer to the pest control report for possible comments.

# 59 Plumbing

Gas Supply:

Iron piping was installed and servicing the building fuel/gas distribution.

Water Supply:

The water source for the building appeared to be supplied by the local municipal service.  Copper water supply service piping was installed where visible.  During the course of the inspection, the water was run (unless the service was shut-off) for the purpose of detecting leakage in the supply and drain/waste system.  This was generally a visual inspection of the system and was not intended to be a technically exhaustive evaluation.  No comment regarding low water flow has been made unless it appeared to the inspector to be uncommonly low;  Since this is a subjective determination, it is strongly recommended that interested parties run the water in the house and make their own determination as to normal or possible low water flow.

Angle stops (the valves located in the cabinet below or adjacent to a faucet) and service valves are inspected for current leakage but are not tested or operated during the course of inspection.  The valves are installed as a service device and are infrequently operated, therefore, care should be taken when they are used since they may be stiff or inoperable and may begin to leak once turned.

Drain/Waste & Venting:

ABS (Acrylonitrile-Butadiene-Styrene) piping was installed at the drain / waste system.  A small percentage of ABS piping in this area has been included in class-action litigation regarding inferior materials and generally applies to piping after September 1985.  WellHouse has made a visual examination as to the condition on the date of inspection and no attempts to identify the manufacturer or date of manufacture to determine if this applies to this particular building.  Interested parties should obtain the services of a licensed plumping contractor to pursue this type of information.

Observed Plumbing Conditions:

60  Garage:  Leaking due to a cracked pipe was noted in an ABS drain line located at the bathroom area(s).  Repair by a licensed plumber is  needed and recommended.

61  Dripping and/or leaking was noted at the hose bib (faucets) visible at the left exterior.  Repair by a qualified plumber in needed.

62  Leaking was noted at the landscape water supply system valves located at the back-right exterior.

63  The drain/wastes lines throughout the house appeared to have been modified and reinstalled.  These appeared to have been improperly installed and numerous places and included S-traps at the sinks, no drain vents, and plugged/capped drain vents.  Further inspection and repairs by a licensed plumber is recommended.

64   Basement: a gas service valve was noted near the water heater tank not currently being used and was not capped.  Capping the valve is recommended.

Observed Plumbing Conditions: (continued)

65  Kitchen: An S-trap was visible at the kitchen sink drain, visible beneath the sink area.  This is an improper and non-code complying condition.  It is recommended to modify the drain line as needed to provide and maintain a P- trap.

66  Downstairs Bath: Leaking was noted at the bath tub drain assembIy including the drain and/or drain overflow and visible from beneath the unit.  Have a qualified plumber repair as needed.

67  Downstairs Bath: An S-trap was visible at the bathroom sink drain, visible beneath the sink area.  This is an improper and non-code complying condition.  It is recommended to modify the drain line as needed to provide and maintain a P- trap.

68  Downstairs Bath: The bath tub drain stop was not operable when examined at the time of inspection.

69  Upstairs Hall Bath: An S-trap was visible at the bathroom sink drain, visible beneath the sink area.  This is an improper and non-code complying condition.  It is recommended to modify the drain line as needed to provide and maintain a P- trap.

70  Bathroom (at the studio): An S-trap was visible at the bathroom sink drain, visible beneath the sink area.  This is an improper and non-code complying condition.  It is recommended to modify the drain line as needed to provide and maintain a P- trap.

71  Kitchen: An S-trap was visible at the kitchen sink drain, visible beneath the sink area.  This is an improper and non-code complying condition.  It is recommended to modify the drain line as needed to provide and maintain a P- trap.

72  Attic Furnace: The service valve was not accessible Inspection by a licensed heating contractor is recommended.

General Plumbing Comments:

73  It is recommended to have a qualified plumber repair/modify as needed.

# 74 Electrical

Service / Panels & Disconnects

The electrical service to the building was located /installed as an overhead "service drop".  The service entry provided by the local utility was 3 wire - 110/220 volts.  The service conductors were not visible when inspected.

Main Electrical Panel

The method or type of wiring installed was generally ungrounded with grounds noted non-metallic sheathed cable and knob and tube where visible.  Access for inspection of the panel was good and visual inspection included removal of the face plate.  The size / amp capacity of the main electrical panel was 100 with circuit breaker over current protection device(s) installed.  The ratings were determined by markings on the panel and/or disconnect.  Grounding of the main panel was noted, see below.  Bonding (connection of the ground) of the panel was noted when inspected.  The primary grounding source for the electrical system appeared to be a ground rod when examined.  Over current protection at the panel branch circuits was provided by circuit breakers.

Interior Sub-panel

Access for inspection of the was good and visual inspection included removal of the dead front face plate.  The installed distribution wiring servicing the 110 volt circuits appeared to be generally copper where visible.  An electrical sub-panel was installed.  Over current protection at the branch circuits was provided by circuit breakers.

Basement Sub-panel

The electrical panel was not accessible for inspection because of a refrigerator and no opinion was rendered regarding it's condition.  Access to the panel should be maintained and the panel remain unlocked.  Inspection of this panel is recommended once access is provided.  An additional fee will be charged for a return trip to the property.

Other Electrical:

Triplex (three prong) grounded electrical receptacle(s) were installed at the varied.

Observed Electrical Conditions:

75  An electrical outlet visible near the upstairs electrical sub-panel was installed into the wood paneling without an electrical junction box.  This is a potentially unsafe condition.

76  Interior Sub-panel: Wiring was noted which was not secured / clamped to the panel box at the entrance to the panel.  Securing the building wiring at this location is standard practice and is intended to protect the wiring connections and/or sheathing from movement.  Have a licensed electrical contractor repair as needed.

77  Interior Sub-panel: Ground conductors were noted inside the panel which were loose and/or not connected.  Have an electrician further inspect and repair as needed to provide / maintain a safe installation.

78  Kitchen: Sink Cabinet:  The junction box was loose when examined.

Observed Electrical Conditions: (continued)

79  A non-weather resistant outlet cover was noted at the electrical outlet(s) and included the back exterior,  This is in need of repair/ modification including the installation of a weather cover for safety reasons.

80  Below the stove and Garage:  The electrical cover plate was missing which resulted in unprotected openings into the electrical box and presents a safety concern.  Repairing this condition is recommended to maintain safe operation.

81  Exterior:  Unprotected surface wiring was noted at the building and visible at the right storage closet.

82  Exterior:  Electrical receptacles which tested as not being GFCI protected were not the original installation and appeared to have been added since grounded GFCI protected electrical receptacles were a requirement and visible at the various exterior.  Have a qualified electrician modify as needed to provide for safe operation.

83  Improper electrical connections and wiring was noted in varied places and included the garage, attic, and interior cabinets and/or closets.  Further inspection/repair by a licensed electrician is recommended.

84  Kitchen: A loose connection between an electrical junction box and conduit was noted below the sink.  Unprotected and exposed electrical conductors were noted and at risk of physical harm.  Repair is recommended to correct this UNSAFE condition.

85  Main Electrical Panel: The circuits at the panel (i.e.: stove, dryer, disposal, etc...) was partially labeled to identify the function of each circuit as would be generally required.

86  Main Electrical Panel: The grounding of the main electrical panel appeared to be installed with non-standard ground rod when examined.  Further investigation by a licensed electrician is recommended.

87  Garage:  An open / uncovered electrical J-box was noted and located at the ceiling framing(s).  This is generally considered as a minor condition, however, it should be covered / protected to provide/maintain a safe installation.

88 Garage:  Unprotected surface wiring located within 7 feet of the floor was noted and visible at the interior surfaces.  Building standards would generally require surface wiring to be protected when located within 7 feet (8 feet in some municipalities) of the garage floor.

89  Basement: An open / uncovered electrical junction box was noted and located at the various area(s).  This is generally considered as a minor condition, however, it should be covered / protected to provide/maintain a safe installation.

90  Basement: Electrical wiring was noted at the various area(s) which had minimal / insufficient support.  The wiring should be properly supported to the building members to prevent premature deterioration and/or damage due to conditions including possible moisture or physical harm.  Have a licensed electrical contractor provide needed repairs.

Observed Electrical Conditions: (continued)

91  Downstairs Bath: Ungrounded triplex receptacle(s) were noted when inspected.  The outlet appeared to be serviced with a 3 wire (grounded) system, therefore the cause for the outlet testing ungrounded was unknown.  This may be due to a loose wire connection at the outlet and/or in a remote location.  Further inspection by a licensed electrical contractor is recommended.

92  Upper Room: Unprotected surface wiring was noted and was visible at the closets.  Building standards would generally require wiring located in habitable areas be protected from physical harm for safety purposes.  Wiring placed in the wall cavity or in a conduit is the most common means of providing protection.

93  Main Electrical Panel: Improper color coding was noted at the panel wiring and included white as hot conductors.  Building standards dictate white colored conductors to be neutral, green or bare metal as ground, and black, red or other colored wires as hot.

94  A/C Right Unit: The electrical conduit connection to the appliance was loose and not moisture proof when examined.  This presents a current safety concern and repair is recommended to provided / maintain a safe installation.

General Electrical Comments:

95  Main Electrical Panel: Evidence was noted when the electrical panel was examined to indicate that it may have been changed since the original construction.  Review of pertinent permits regarding possible changes by interested parties is recommended.

96  Interior Sub-panel: Evidence was noted when the electrical panel was examined to indicate that it may have been changed since the original construction.  Review of pertinent permits regarding possible changes by interested parties is recommended.

97  While the electrical outlet(s) in wet locations appeared to have been installed prior to current standards requiring GFCI protected circuits in wet locations, the addition of a GFCI, outlet or circuit breaker, is recommended as a safety upgrade.  This should be relatively inexpensive and would significantly increase the degree of safety while using electrical appliances.  It is recommended to refer to a licensed electrical contractor for additional information and pricing.

98   It is recommended to have a qualified contractor repair/modify as needed.

# 99 Mechanical

Water Heater:

A natural gas fired water heater was installed and had a rating of undetermined BTU's (British Thermal Units).  A thermostat was installed at the unit which will control the water temperature by cycling the burner on/off.  The higher the temperature setting, the hotter the water and higher the energy consumed.  Inversely, the lower the temperature is kept, the more economical the unit will be to operate.  The temperature setting is ultimately a personal choice and will likely require some experimenting, however, care should be taken to not set the temperature so hot as to be unsafe.  The tanks approximate age was 10 - 15 years and the capacity was 40 gallons.  The water heater unit was located at the basement area.  A T&P (temperature and pressure relief) valve was noted, see below at the tank and an overflow pipe was not installed, see below.  A single wall metal and rated aluminum flex flue was noted above the unit.  A draft diverter (hood) was installed.  The draft hood is located on top of the tank above the units vent opening and has the flue connected to it with the purpose of promoting/maintaining proper venting.  Seismic bracing of the tank was not properly installed.

Heating / Cooling:

The unit was located in the basement.  HVAC supply-air ducting was installed to distribute conditioned air from the supply plenum of the furnace to the boots (registers at the interior).  Fiberglass duct insulation was generally installed and was wrapped at the exterior surfaces.  The supply boots (registers) were generally not visible.

Attic Furnace

A natural gas fired forced-air furnace was installed and had an input rating of 80,000 BTU's (British Thermal Units).  The unit was located in the attic.  Access to the furnace located in the attic appeared to be at adequately sized.  The approximate age of the unit appeared to be 20 - 25 years.  A standard thermostat was installed at the building interior to control the units operation.  The air-filter was disposable and located at the furnace blower compartment.  While it is important to keep the air-filter clean, the frequency for cleaning and/or replacement will vary depending on personal use and local conditions.  It is a good idea to check the filters monthly until a maintenance pattern is established.  The standing pilot was installed to light the units burners.  A metal heat exchanger was installed as part of the furnace assembly with the purpose of transferring heat through the metal while preventing combustion gases from mixing with the house air flowing along side the heated surface.  A blower fan was installed to circulate the house air through the furnace to be heated and then to the house interior.  A single wall metal flue was installed at and services the furnace.

Basement Furnace

A natural gas fired forced-air furnace was installed and had an input rating of 100,000 BTU's (British Thermal Units).  The approximate age of the unit appeared to be 20 - 25 years.  A standard thermostat was installed at the building interior to control the units operation.  The air-filter was disposable and located at the furnace blower compartment.  While it is important to keep the air-filter clean, the frequency for cleaning and/or replacement will vary depending on personal use and local conditions.  It is a good idea to check the filters monthly until a maintenance pattern is established.  The standing pilot was installed to light the units burners.  A metal heat exchanger was installed as part of the furnace assembly with the purpose of transferring heat through the metal while preventing combustion gases from mixing with the house air flowing along side the heated surface.  A blower fan was installed to circulate the house air through the furnace to be heated and then to the house interior.  A single and double wall vent flue was installed at and services the furnace.

A/C Units

Central air-condition was installed as part of the split forced-air HVAC system.  A condenser unit was installed at the exterior and located at the left side and at the right side exterior.  An air-handler unit was installed adjacent to the furnace/heater unit and contains evaporator coils where cold refrigerant flows through and warm (unconditioned) air blows across to be cooled.  Provisions for drainage of the condensation water, which collects during operation, was noted.  Refrigerant lines were visible and function to connect between the condenser unit and evaporative coils.  Refrigerant, commonly Freon, flows through the closed loop system with "cold" refrigerant sent to the air-handlers evaporative coils and "warm" refrigerant returned to the condenser to be recooled.  Commonly these are identifiable by the cold supply  lines being insulated and the return lines not.

Observed Mechanical Conditions:

100  Water Heater:  While provisions for anchoring (seismic strapping) was noted at the water heater unit, it was improperly installed to provide adequate support of the unit according to current local building standards, see comments below.

101  A temperature / pressure relief (TP) valve was plugged when examined.  A TP valve device is a SAFETY device and should  be maintained as functional for safe operation.  Refer to a qualified plumber.

102  The vent flue of the water heater unit was improper when examined and included insufficient upward slope.  Modification / repair is should be done to provide/maintain proper venting of the combustion gases and safe operation.

103  The single wall and flex metal water heater flue vent was installed with insufficient clearances to combustible materials including the floor framing and floor sheathing and wall framing and siding.  This condition is in need of modification / repair to provide safe operation and should include minimum clearances of one (1) inch for type B, six (6) inches for single wall rated vents and eighteen (18) inches for non-rated vents.  It is recommended to have a qualified contractor repair/modify as needed.

104  Improper vents/flue assemblies were noted at both furnaces and at the water heater.  Current health and fire hazards were noted associated with the installations.  Further inspection and repair for safety reasons is recommended by a licensed heating contractor.

105  A/C Left Unit: The air-conditioning units clearances appeared to be minimal / insufficient and included less than 12 inches at the side(s) of the unit.  The minimum clearances may vary between manufactures, however, 6 feet above and 12 inches at the sides are generally needed to maintain adequate air-flow around the unit and maintain proper operation.

106  A/C Right Unit: Air-conditioner: A broken grill was noted at the air-conditioning condenser when inspected.  There was no visible damage to the coils in behind the grill, however, repair to the grill is recommended to provide SAFE operation.

107  Basement Furnace: The vent flue of the furnace was improper when examined and included insufficient upward slope.  Modification / repair is should be done to provide/maintain proper venting of the combustion gases and safe operation.

Observed Mechanical Conditions: (continued)

108  Attic Furnace: The single wall furnace flue vent was installed with insufficient clearances to combustible materials including the roof sheathing and roof framing and insulation.  This condition is in need of modification / repair to provide safe operation and should include minimum clearances of one (1) inch for type B, six (6) inches for single wall rated vents and eighteen (18) inches for non-rated vents.  It is recommended to have a qualified contractor repair/modify as needed.

109  Basement Furnace: The double wall, type B and single wall furnace flue vent was installed with insufficient clearances to combustible materials including the wall framing and floor sheathing.  This condition is in need of modification / repair to provide safe operation and should include minimum clearances of one (1) inch for type B, six (6) inches for single wall rated vents and eighteen (18) inches for non-rated vents.  It is recommended to have a qualified contractor repair/modify as needed.

110  Attic Furnace: The furnace vent (flue) joints were taped with a non-heat resistant tape which is an improper installation and a possible fire hazard.

111  Attic Furnace: The furnace was visually examined at the time of inspection including the units heat exchanger when possible.  The unit was fire tested by modifying the temperature setting at the thermostat and appeared to be in generally serviceable condition at the time of inspection except as otherwise noted.  A build-up of corrosion was noted on the interior surfaces of the metal heat exchanger when examined.  Cleaning the exchanger and reexamined and testing is recommended.  Refer to a qualified heating contractor.

General Mechanical Comments:

112  Seismic anchoring / strapping is currently required on all water heaters in California as a health and safety requirement.  The Town of Los Gatos requires water heaters to be anchored or strapped to resist horizontal displacement due to earthquake motion as per specified in the 1994 Uniform Plumbing Code.  Strapping shall be at points within the upper one-third (1/3) and lower one-third (1/3) of its vertical dimensions.  At the lower point, a minimum distance of four (4) inches shall be maintained above the controls with the strapping.  For more specific information and diagrams, refer to the Los Gatos building department (408-354-6876) and/or the Office of the State Architect (916-324-5315).

113  A/C Both Units: The air-conditioning system was not tested because the ambient (outdoor) temperatures were colder than 60 degrees Fahrenheit at the time of inspection.  Running the unit in cold temperatures may damage the equipment and should be avoided.  The unit should be tested prior to the close of escrow, if possible, to verify operation.  When running, the suction refrigerant line (usually insulated and larger in diameter) near the unit should be cold to the touch and the liquid line (smaller in size and not insulated) should feel warm (not hot) to the touch.

114  Attic Furnace: The furnace has hard piping installed at the connection between the unit and gas supply.  A flexible gas appliance connector is recommended to be added to allow for possible slight seismic or other movement without stressing the gas pipe couplings.   However, the flexible appliance connector should not be installed to pass through the furnace housing.  Contact a qualified contractor for this upgrade.

# 115 Chimney(s) & Fireplace(s)

Wood Stove

The fireplace chimney was a manufactured metal chimney flue pipe and had a spark arrestor and rain cap installed when inspected.

Foyer

The fireplace firebox was constructed of masonry firebrick where visible.  The firebox is the area in which wood fuel is burned and is visible from the interior.  It functions to direct smoke upward, reflect heat to the interior room, and to protect the structural chimney brick from the intense heat. A metal damper was not installed at the unit. The (outer) hearth at the fireplace was constructed of  ceramic tile and functions to provide / maintain a fire resistant surface near the fireplace opening.

Observed Chimney/Fireplace Conditions:

116  Wood Stove: The chimney flue appeared to end low relative to the building.  Construction standards generally require the chimney to be a minimum of two feet higher than any building projection located within ten feet of the unit as a provision to maintain proper draw.

117  Foyer: The fireplace firebox had deterioration / loose brick at the interior and was in need of repair when examined.  It is recommended to have a qualified chimney / fireplace contractor inspect and provide an opinion and recommendations for repair.

General Chimney/Fireplace Comments:

118  Foyer: The chimney was examined from the ground only at the time of inspection because of roof access limitations and the unit interior liner was not examined and was not stress tested.  Refer to the roof section of this report for possible related comments.

# 119 Insulation & Ventilation

Insulation:

Glass fiber batt insulation without a moisture barrier was installed at the ceiling/roof area and appeared to have an average depth of approximately 4 to 5 (R-15).  Current local standards would generally have roof / ceiling insulation with R-values usually ranging between R-19 and R-30 (with the larger "R" value indicating more insulation).

# 120 End

please read carefully

agreement for home inspection services

1.	As requested by John & Jane Lucky (hereafter called client), WellHouse Corporation (hereafter called WellHouse) has performed a visual home inspection of 130 OldhouseAve., Los Gatos, CA, on 3/18/98 for a service fee in the amount of $650.  WellHouse is providing this written report identifying the present condition of the below stated items.  This inspection will be of readily accessible areas of the house and is limited to visual observations of apparent conditions which were existing at the time of the inspection.  The inspector is not required to move personal property, debris, furniture, equipment, carpeting or like materials which may impede access or limit visibility.  Items or conditions which are latent or concealed are excluded from the inspection.  The inspection is not intended to be technically exhaustive.  Equipment and systems will not be dismantled.  The inspection includes only the items and systems expressly and specifically identified as follows:

* Drainage	* Interior	* Heating	* Roof

* Foundation	* Materials of Construction	* Crawlspace/basement	* Insulation

* Electrical	* Attic	* Fireplace(s)	* Appliances

* Plumbing	* Central Air Conditioning 	* Driveway/walkways 	* Exterior

Window operation and electrical outlets, switches, and fixtures are checked by random sampling.  Garage doors and garbage disposers are checked for operation only.  Only the dishwasher's ability to fill and drain properly is checked.  Thermostats and timers are not checked for accuracy.  Air conditioners are checked for equipment operation only.

2.	The inspection and report will be performed in a  manner consistent with the Standards of Practice of the American Society of Home Inspectors (ASHI).  The inspection and report are performed and prepared for the client.  WellHouse accepts no responsibility for misinterpretation by third parties.

3.	Items and systems NOT INCLUDED in the inspection are as follows:

* service utilities	* playground equipment	* pools/pool equipment	* sidewalks

* wells/springs	* tennis courts	* detached buildings 	* elevators

* solar systems	* security systems	* recreational appliances	* septic tanks

* personal property	* cosmetic items	* drainfields	* water softeners

* sprinkler system	* central vacuum	* cesspools	* fences

4.	The inspection/report is NOT a compliance inspection for past or present governmental codes or regulations of any kind.  Though the building codes are a standard for some of our evaluation, by definition, such inspections can only be performed by the building department of local jurisdiction.

5.	The inspection and report DO NOT ADDRESS AND ARE NOT INTENDED TO ADDRESS THE POSSIBLE PRESENCE OF OR DANGER FROM ELECTRICAL LINES, POLES, OR TRANSFORMERS, RADON GAS, LEAD PAINT, UREA FORMALDEHYDE, TOXIC OR FLAMMABLE CHEMICALS, WATER OR AIRBORNE RELATED ILLNESS OR DISEASE, AND ALL OTHER SIMILAR OR POTENTIALLY HARMFUL SUBSTANCES.  Client is urged to contact a reputable specialist if information, identification or testing for the above is desired.

6.	This inspection/report is not intended to be used as a guarantee or warranty, expressed or implied, regarding the adequacy, performance or condition of any inspected structure, item or system.  The inspection and report are not intended to reflect the value of the premises, nor to make any representation as to the advisability or inadvisability of purchase or the suitability for use.

7.	This inspection is not an insurance policy.  The inspection/report is not a certification of any kind.  WellHouse shall not be construed as insuring against any defects or deficiencies not contained in the inspection report and subsequently discovered.

8.	WellHouse will not be held liable for any claims without reasonable notification and opportunity to reinspect the condition(s) in dispute prior to any change or modification to the said condition(s).

The client is immediately to put in writing to WellHouse problems with the service.  Communications must be consistent in that the party originally accompanying the inspector will be the party resolving any disputes.

Any controversy or claim arising out of or related to this contract, or any breach thereof, shall be settled by arbitration in accordance with the rules of the American Arbitration Association, and judgment upon award rendered by the arbitrators may be entered in any court having jurisdiction.  Disputes settled without favor to the client will mandate a payment of reinspection time, fees and arbitration costs.

9.	Payment is due upon completion of the on-site inspection unless arrangements for escrow billing were made prior to the inspection.  There will be a $20.00  charge if any form of payment is subsequently dishonored.  All legal and time expenses incurred in collecting due payments, returned checks, or unaccepted credit and payments will paid by the purchaser of the service.  Any fee not paid within 30 days of the inspection will have a service charge of 1.5% monthly or 18% per annum added to the inspection fee.  Credit is on an approval basis

This agreement represents the entire agreement between the parties.  No change or modification shall be enforceable against any party unless such change or modification is in writing and signed by the parties.  This agreement shall be binding upon and enforceable by the parties, and their heirs, executors, administrators, successors and assigns.